## Slide 1
CHARACTERISTICS
GUOWANG CABLE
We have world-class testing facility, and made rigorous testing regime, every meter of cable before leaving the factory must
go through strict testing, testing qualiﬁed products will be shipped to customers, effectively ensure product quality and meet customer requirements.
N2XS(FL)H 18/30 (36)kV Cable
GUOWANG
CABLE GROUP
Class 2 Stranded Copper
XLPE (Cross-Linked Polyethylene)
Focused Professional Integrity Win-win
technicalspeciﬁcation 1 of 3
THE CABLE TEST
CONSTRUCTION
Conductor Screen
Insulation Screen
Conductor
Insulation
Guowang Cable actively implements the "carbon reduction" goal, strives to promote the green's low-carbon transformation, strengthens energy-saving and emission reduction technology innovation, and promotes the company's healthy and sustain- able development.
SUSTAINABILITY COMMITMENT
Voltage Rating Uo/U (Um)
18/30 (36)kV
IEC 60502-2, IEC 60228,
Low Smoke Zero Halogen: IEC 60754-1/2, IEC 61034-2
Flame Retardant: EN 60332-3-24 Cat C, IEC 60332-1-2
UV Resistant: EN 50396
Abrasion and Tear Resistant: EN 60229-4.1
Impact rated to: AG2 EN 60364-5.5
APPLICATION
Medium voltage power cables for distribution networks and generation units. LSZH outer sheathing makes the cable
suitable for internal installation as well as directly in ground, outdoors, and in cable ducts. UV Resistant.
CHARACTERISTICS
STANDARDS
Semi-conductive material
Semi-conductive material (bonded)
Longitudinal Waterblocking
Semi-conductive swellable tape
Screen
Copper Wires and copper tape
Longitudinal Waterblocking
Swellable Tapes
Radial Waterblocking
Al/PET (Aluminium/Polyester) tape tightly bonded to sheath
Sheath Colour
Black
Test Voltage:
63kV AC 50Hz (15 mins)
Temperature Rating
-20°C to +60°C
Permissible Conductor Operating Temperature: +90°C
Permissible Short Circuit Temperature up to 5 sec: 250°C
Minimum Bending Radius
15 x overall diameter
Outer Sheath
LSZH (Low Smoke Zero Halogen)

## Slide 2
GUOWANG CABLE GROUP
Professional Integrity Win-win
2 of 3 technicalspeciﬁcation
DIMENSIONS
Focused
GUOWANG CABLE
NO. OF CORE | NOMINAL CROSS SECTIONAL AREA |  | NOMINAL Conductor DIAMETER | NUMBER WIRES CONDUCTOR | NOMINAL THICKNESS SEMI-CON. LAYER INNER OUTER |  | NOMINAL INSULATION THICKNESS | MINIMUM INSULATION THICKNESS | NOMINAL DIAMETER OVER INSULATIOIN
 | Conductor | Screen | mm | mm | mm | mm | mm | mm | mm
1 | 50 | 16 | 8.1 | 10*2.62 | 0.5 | 0.4 | 8 | 7.1 | 25.1
1 | 70 | 16 | 9.7 | 14*2.62 | 0.5 | 0.4 | 8 | 7.1 | 26.7
1 | 95 | 16 | 11.4 | 19*2.62 | 0.5 | 0.4 | 8 | 7.1 | 28.4
1 | 120 | 16 | 12.7 | 19*2.97 | 0.5 | 0.4 | 8 | 7.1 | 29.7
1 | 150 | 25 | 14.5 | 19*3.20 | 0.5 | 0.4 | 8 | 7.1 | 31.5
1 | 185 | 25 | 15.9 | 37*2.62 | 0.5 | 0.4 | 8 | 7.1 | 32.9
1 | 240 | 25 | 18.6 | 48*2.62 | 0.5 | 0.4 | 8 | 7.1 | 25.6
1 | 300 | 25 | 20.7 | 61*2.62 | 0.5 | 0.4 | 8 | 7.1 | 37.7
1 | 400 | 35 | 23.5 | 61*2.97 | 0.5 | 0.4 | 8 | 7.1 | 40.5
1 | 500 | 35 | 26.5 | 61*3.29 | 0.5 | 0.4 | 8 | 7.1 | 43.5
1 | 630 | 35 | 30.2 | 61*3.80 | 0.5 | 0.4 | 8 | 7.1 | 47.7
NOMINAL CROSS SECTIONAL AREA | NUMBER WIRES SCREEN | DIAMETER TAPE SCREEN | NOMINAL SHEATH THICKNESS | MINIMUM SHEATH THICKNESS | NOMINAL OVERALL DIAMTER | NOMINAL WEIGHT | MAXIMUM SIDEWALL PRESSURE | MAXIMUM PULLING TENSION
mm2 | mm | mm | mm | mm | mm | kg/km | N/cm2 | N
50 | 44*.066 | 1*0.1*10 | 2.0 | 1.40 | 32 | 1400 | 416 | 2500
70 | 44*0.66 | 1*0.1*10 | 2.0 | 1.40 | 34 | 1600 | 534 | 3500
95 | 44*.066 | 1*0.1*10 | 2.1 | 1.48 | 36 | 1900 | 668 | 4750
120 | 44*0.66 | 1*0.1*10 | 2.1 | 1.48 | 37 | 2250 | 805 | 6000
150 | 71*0.66 | 1*0.1*10 | 2.2 | 1.56 | 39 | 2750 | 935 | 7500
185 | 71*0.66 | 1*0.1*10 | 2.2 | 1.56 | 40 | 3000 | 1103 | 9250
240 | 71*0.66 | 1*0.1*10 | 2.3 | 1.64 | 43 | 3750 | 1299 | 12000
300 | 71*0.66 | 1*0.1*10 | 2.4 | 1.72 | 46 | 4250 | 1499 | 15000
400 | 60*0.85 | 1*0.1*1.5 | 2.5 | 1.80 | 49 | 5250 | 1939 | 20000
500 | 60*0.85 | 1*0.1*1.5 | 2.6 | 1.88 | 52 | 6250 | 2123 | 25000
630 | 60*0.85 | 1*0.1*1.5 | 2.7 | 1.96 | 56 | 7750 | 2436 | 31500

## Slide 3
NOMINAL CROSS SECTIONAL AREA mm² | CONDUCTOR DC RESISTANCE AT 20°C Ω/km | CONDUCTOR DC RESISTANCE AT 75℃ Ω/km | CONDUCTOR AC RESISTANCE BY MAX TEMP. Ω/km | NOMINAL INSULATION THICKNESS In Ground InAir 20℃ 30℃ | REACTANCE ohms/km | CHARGING ADMITTANCE A/km | CAPACITANCE uF/km | S.C.C CONDUCTOR 1SEC kA | CONDUCTOR LOSSES IN THE GROUND
50 | 0.387 | 0.801 | 0.497 | 251 279 | 0.20 | 0.44 | 0.12 | 7.15 | 31.3
70 | 0.268 | 0.555 | 0.344 | 306 348 | 0.20 | 0.41 | 0.13 | 10.1 | 32.2
95 | 0.193 | 0.399 | 0.248 | 363 521 | 0.19 | 0.39 | 0.14 | 13.59 | 32.7
120 | 0.153 | 0.316 | 0.196 | 410 483 | 0.18 | 0.38 | 0.15 | 17.16 | 32.9
150 | 0.124 | 0.256 | 0.160 | 449 540 | 0.18 | 0.36 | 0.17 | 21.45 | 32.3
185 | 0.0991 | 0.205 | 0.128 | 503 615 | 0.18 | 0.35 | 0.18 | 26.46 | 32.4
240 | 0.0754 | 0.156 | 0.0980 | 576 718 | 0.17 | 0.34 | 0.20 | 34.32 | 32.5
300 | 0.0601 | 0.124 | 0.0800 | 641 812 | 0.17 | 0.32 | 0.21 | 42.90 | 32.9
400 | 0.0470 | 0.0974 | 0.0640 | 697 904 | 0.16 | 0.31 | 0.24 | 57.20 | 31.1
500 | 0.0366 | 0.0758 | 0.0510 | 768 1011 | 0.16 | 0.30 | 0.26 | 71.50 | 30.1
630 | 0.0283 | 0.0586 | 0.0420 | 850 1030 | 0.16 | 0.29 | 0.29 | 90.09 | 30.3
GUOWANG CABLE GROUP
Professional Integrity Win-win
3 of 3 technicalspeciﬁcation
Focused
GUOWANG CABLE
ELECTRICAL CHARACTERISTICS
Derating factor (ground): 1 (Soil thermal resistivity: 1km/W, Depth 0.8m, Flat formation - touching)
Derating factor (air): 1 (Flat formation - touching)
The information contained within this datasheet is for guidance only and is subject to change without notice or liability. All the information is provided in good faith and is believed to be correct at the time of publication. When selecting cable accessories, please note that actual cable dimensions may vary due to manufacturing tolerances.